## 8BF-TRT日报表
炼 铁 厂 （ 8# ）TRT 系 统 运 行 记 录
编号：SGSSG-BSMCSA30-G031-03A
| 透平煤气参数 |  |  |  | 透平机参数 | [10 empty] | 发电机参数 |  |  |  |  | 动力油系统 |  |  |  | 润滑系统 |  |  |  | 记事栏
| 入口 压力 kPa | 入口 温度 ℃ | 出口 压力 kPa | 出口 温度 ℃ | 透平转速r/min | 轴位移 A值 mm | 轴位移 B值 mm | 前轴 振动 A值 μm | 前轴 振动 B值 μm | 后轴 振动 A值 μm | 后轴 振动 B值 μm | 止推轴 承主推 力瓦温 度A（℃） | 止推轴 承付推 力瓦温 度B（℃） | 前轴 承温 度（℃） | 后轴 承温 度（℃） | 有功功 率MW | 前轴 承温 度（℃） | 后轴 承温 度（℃） | 轴承 振动 A（mm/s） | 轴承 振动 B（mm/s） | 供油 压力 MPa | 危机 保安 油压 MPa | 油箱 液位 mm | 油箱 温度 ℃ | 远点 油压 MPa | 油箱 液位 mm | 油箱 温度 ℃ | 冷却 出口 温度 ℃
报警 |  | 200 |  | ＜50 | 3150 | ≥0.4≤-0.5 | ≥0.4≤-0.5 | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 90 |  | 85 | 85 | 7.5 | 7.5 | 11 |  | 500 | ＜20 ＞60 | 0.14 | 620 | ＜30 ＞60 | 45
停机 |  | 250 |  |  | 3240 | ≥0.6≤-0.7 | ≥0.6≤-0.7 | 130 | 130 | 130 | 130 | 105 | 105 | 100 | 100 |  | 95 | 95 | 11.5 | 11.5 | 9 | 2.5 |  |  | 0.08
| BF8_L2C_TRT_Turbine_In_Pressure_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Temperature_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Pressure_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Temperature_BF8_1m_avg | BF8_L2C_TRT_Turbine_Speed_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axes_Offset_A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axes_Offset_B_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axial_T_1A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axial_T_1B_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_S_T202A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_S_T203A_BF8_1m_avg | BF8_L2C_TRT_GeneratorActivePower_BF8_1m_avg | BF8_L2C_TRT_Generator_1_Bearing_T_BF8_1m_avg | BF8_L2C_TRT_Generator_2_Bearing_T_BF8_1m_avg | BF8_L2C_TRT_Generator_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Generator_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_PowerOil_Pressure_BF8_1m_avg | BF8_L2C_TRT_FastCloseValvePowerOil_P_BF8_1m_avg | BF8_L2C_TRT_PowerOilBox_Level_BF8_1m_avg | BF8_L2C_TRT_PowerOilBox_Temperature_BF8_1m_avg | BF8_L2C_TRT_LubricatingOil_Pressure_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilBox_Level_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilBox_T_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilCooler_T_BF8_1m_avg
0 | [28 empty] | 发电量底数： kWh 本班发电量： kWh 值班人：
1
2
3
4
5
6
7
8 | [28 empty] | 发电量底数： kWh 本班发电量： kWh 值班人：
9
10
11
12
13
14
15
16 | [28 empty] | 电量底数： kWh 本班发电量： kWh 值班人：
17
18
19
20
21
22
23

## _tag_day_all
BF8_L2C_TRT_Turbine_In_Pressure_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Temperature_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Pressure_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Temperature_BF8_1m_avg | BF8_L2C_TRT_Turbine_Speed_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axes_Offset_A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axes_Offset_B_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axial_T_1A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Axial_T_1B_BF8_1m_avg | BF8_L2C_TRT_Turbine_In_S_T202A_BF8_1m_avg | BF8_L2C_TRT_Turbine_Out_S_T203A_BF8_1m_avg | BF8_L2C_TRT_GeneratorActivePower_BF8_1m_avg | BF8_L2C_TRT_Generator_1_Bearing_T_BF8_1m_avg | BF8_L2C_TRT_Generator_2_Bearing_T_BF8_1m_avg | BF8_L2C_TRT_Generator_Axes_X_BF8_1m_avg | BF8_L2C_TRT_Generator_Axes_Y_BF8_1m_avg | BF8_L2C_TRT_PowerOil_Pressure_BF8_1m_avg | BF8_L2C_TRT_FastCloseValvePowerOil_P_BF8_1m_avg | BF8_L2C_TRT_PowerOilBox_Level_BF8_1m_avg | BF8_L2C_TRT_PowerOilBox_Temperature_BF8_1m_avg | BF8_L2C_TRT_LubricatingOil_Pressure_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilBox_Level_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilBox_T_BF8_1m_avg | BF8_L2C_TRT_LubricatingOilCooler_T_BF8_1m_avg

## _dictionary
version | 8